## Sheet1
Type | 48NPFC10 | 48NPFC10 Micro | 48NPFC20 | 48NPFC20 Micro | 48NPFC50 | 48NPFC80 | 48NPFC100
std capacity Ah C/5 | 10 | 10 | 20 | 20 | 50 | 80 | 100
Energy content 100% SOC (kWh) | 0.48 | 0.48 | 0.96 | 0.96 | 2.4 | 3.84 | 4.8
Usable Energy content 80% SOC (Wh) | 0.384 | 0.384 | 0.768 | 0.768 | 1.92 | 3.072 | 3.84
Dimensions:
19" Frame | yes |  | yes |  | yes | yes | yes
Weight kg | 7.3 |  | 13.4 |  | 32 | 44 | 45
Weight Density Ah/kg | 1.3699 |  | 1.4925 |  | 1.5625 | 1.8182 | 2.2222
Weight Density Wh/kg | 65.7534 |  | 71.6418 |  | 75 | 87.2727 | 106.6667
Width | 442 |  | 442 |  | 442 | 442 | 443
Height | 44 |  | 88 |  | 132.5 | 225 | 225
Depth | 245 |  | 245 |  | 390 | 400 | 400
Charge / Discharge:
Nominal Voltage | 48 |  | 48 |  | 48 | 48 | 48
Charge Voltage @ 80% | 54 |  | 54 |  | 54 | 54 | 54
Charge Voltage @ 100% | 5400% |  | 5400% |  | 5400% | 5400% | 5400%
Max charge current (A) | 1000% |  | 2000% |  | 4000% | 6000% | 6000%
Max discharge current (A) | 10 |  | 20 |  | 40 | 60 | 60
Voltage range @ 80% | 40.5 -54 |  | 40.5 -54 |  | 40.5 -54 | 40.5 -54 | 40.5 -54
Voltage range @ 100% | 40.5 -54 |  | 40.5 -54 |  | 40.5 -54 | 40.5 -54 | 40.5 -54
Charge temperature optimal | 15 to 35℃ |  | 15 to 35℃ |  | 15 to 35℃ | 16 to 35℃ | 17 to 35℃
Charge temperature Maximum | 0 to 60℃ |  | 0 to 60℃ |  | 0 to 60℃ | 1 to 60℃ | 2 to 60℃
Discharge temperature Optimal | 15 to 35℃ |  | 15 to 35℃ |  | 15 to 35℃ | 16 to 35℃ | 17 to 35℃
Discharge temperature Maximum | -20 to 60℃ |  | -20 to 60℃ |  | -20 to 60℃ | -20 to 60℃ | -20 to 60℃
Lifetime @ float | 12 years |  | 12 years |  | 12 years | 13 years | 14 years
Stack | Cabinet/Rack |  | Cabinet/Rack |  | Cabinet/Rack | Cabinet/Rack | Cabinet/Rack
Storage:
3months @ temperature | 0.91 |  | 0.91 |  | 0.91 | 0.91 | 0.91
6months @ temperature | 0.82 |  | 0.82 |  | 0.82 | 0.82 | 0.82
1year @ temperature | NA |  | NA |  | NA | NA | NA
BMS Functions: | Cell over-charge protection
Cell over discharge protection
Discharge over current protection
Charge limit current
Short circuit protection
Temperature protection
Remote monitoring:
GPRS | NA |  | NA |  | NA | NA | NA
RS232 | available |  | available |  | available | available | available
RS485 | available |  | available |  | available | available | available
IP | NA |  | NA |  | NA | NA | NA
CAN | NA |  | NA |  | NA | NA | NA
IP rating | IP20 |  | IP20 |  | IP20 | IP20 | IP20
cycles
25°C
20 DoD | 24000 |  | 24000 |  | 24000 | 24000 | 24000
30 DoD | 17000 |  | 17000 |  | 17000 | 17000 | 17000
40 DoD | 12000 |  | 12000 |  | 12000 | 12000 | 12000
50 DoD | 8500 |  | 8500 |  | 8500 | 8500 | 8500
60 DoD | 6000 |  | 6000 |  | 6000 | 6000 | 6000
70 DoD | 4500 |  | 4500 |  | 4500 | 4500 | 4500
80 DoD | 3500 |  | 3500 |  | 3500 | 3500 | 3500
30°C
20 DoD | 21600 |  | 21600 |  | 21600 | 21600 | 21600
30 DoD | 15300 |  | 15300 |  | 15300 | 15300 | 15300
40 DoD | 10800 |  | 10800 |  | 10800 | 10800 | 10800
50 DoD | 7600 |  | 7650 |  | 7650 | 7650 | 7650
60 DoD | 5400 |  | 5400 |  | 5400 | 5400 | 5400
70 DoD | 4000 |  | 4050 |  | 4050 | 4050 | 4050
80 DoD | 3100 |  | 3150 |  | 3150 | 3150 | 3150
35°C
50 DoD | 6800 |  | 6800 |  | 6800 | 6800 | 6800
60 DoD | 4800 |  | 4800 |  | 4800 | 4800 | 4800
70 DoD | 3600 |  | 3600 |  | 3600 | 3600 | 3600
80 DoD | 2800 |  | 2800 |  | 2800 | 2800 | 2800
cycles
38°C
50 DoD | 6120 |  | 6120 |  | 6120 | 6120 | 6120
60 DoD | 4320 |  | 4320 |  | 4320 | 4320 | 4320
70 DoD | 3240 |  | 3240 |  | 3240 | 3240 | 3240
80 DoD | 2520 |  | 2520 |  | 2520 | 2520 | 2520
cycles
40°C
20 DoD | 16200 |  | 16200 |  | 16200 | 16200 | 16200
30 DoD | 11000 |  | 11000 |  | 11000 | 11000 | 11000
40 DoD | 8100 |  | 8100 |  | 8100 | 8100 | 8100
cycles
45°C
50 DoD | 5100 |  | 5100 |  | 5100 | 5100 | 5100
60 DoD | 3600 |  | 3600 |  | 3600 | 3600 | 3600
70 DoD | 2700 |  | 2700 |  | 2700 | 2700 | 2700
80 DoD | 2100 |  | 2100 |  | 2100 | 2100 | 2100